SECTION 235216 – 399 MBTU CONDENSING BOILERS

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract apply to this Section, including General and Supplementary Conditions and Division 01 Specification Sections.

      - SUMMARY

        - This Section includes packaged, factory-fabricated and -assembled, gas-fired, fire-tube condensing boilers, trim and accessories for generating hot water.

      - SUBMITTALS

        - Product Data: Include performance data, operating characteristics, furnished specialties and accessories.

          - Prior to flue vent installation, engineered calculations and drawings must be submitted to Architect/Engineer to thoroughly demonstrate that size and configuration conform to recommended size, length and footprint for each submitted boiler.

        - Pressure Drop Curve: Submit pressure drop curve for flows ranging from 0 GPM to maximum value of boiler

          - If submitted material is different from that of the design basis, boiler manufacture shall incur all costs associated with reselection of necessary pumps. Possible differences include, but are not limited to, the pump type, pump pad size, electrical characteristics and piping changes.

        - Shop Drawings: For boilers, boiler trim and accessories, include:

          - Plans, elevations, sections, details and attachments to other work

          - Wiring Diagrams for power, signal and control wiring

        - Source Quality Control Test Reports: Reports shall be included in submittals.

        - Field Quality Control Test Reports: Reports shall be included in submittals.

        - Operation and Maintenance Data: Data to be included in boiler emergency, operation and maintenance manuals.

        - Warranty: Standard warranty specified in this Section

        - Other Informational Submittals

          - ASME Stamp Certification and Report: Submit "A," "S," or "PP" stamp certificate of authorization, as required by authorities having jurisdiction, and document hydrostatic testing of piping external to boiler.

      - QUALITY ASSURANCE

        - Electrical Components, Devices and Accessories: Boilers must be listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

        - I=B=R Performance Compliance: Condensing boilers must be rated in accordance with applicable federal testing methods and verified by AHRI as capable of achieving the energy efficiency and performance ratings as tested within prescribed tolerances.

        - ASME Compliance: Condensing boilers must be constructed in accordance with ASME Boiler and Pressure Vessel Code, Section IV “Heating Boilers”.

        - ASHRAE/IESNA 90.1 Compliance: Boilers shall have minimum efficiency according to "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

        - DOE Compliance. Minimum efficiency shall comply with 10 CFR 430, Subpart B, Appendix N, "Uniform Test Method for Measuring the Energy Consumption of Furnaces and Boilers."

        - ETL Certified and Listed to ANSI Z21.13/CSA 4.9 test standards for US and Canada

        - NOx Emission Standards. When installed and operated in accordance with manufacturer’s instructions, condensing boilers shall comply with the NOx emission standards outlined in South Coast Air Quality Management District (SCAQMD), Rule 1146.2; and the Texas Commission on Environmental Quality (TCEQ), Title 30, Chapter 117, Rule 117.465.

      - COORDINATION

        - Coordinate size and location of concrete bases. Cast anchor-bolt inserts into bases. Concrete, reinforcement and formwork requirements are specified in Division 03. (If the floor mount kit is supplied)

      - WARRANTY

        - Standard Warranty: Boilers shall include manufacturer's standard form in which manufacturer agrees to repair or replace components of boilers that fail in materials or workmanship within specified warranty period.

          - Warranty Period for Fire-Tube Condensing Boilers

- The pressure vessel/heat exchanger shall carry a 10-year from shipment, prorated, limited warranty against any failure due to condensate corrosion, thermal stress, mechanical defects or workmanship.

- All other components, with the exception of the igniter and flame detector, are conditionally guaranteed against any failure for 18 months from shipment

- PRODUCTS

      - MANUFACTURERS

        - Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

        - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

        - Basis-of-Design Product: Subject to compliance with requirements, provide AERCO International, EST 399 or a comparable product by one of the following:

          - AERCO International

          - Buderus

          - Viessmann Manufacturing Co. (US) Inc.

      - CONSTRUCTION

        - Description: Boiler shall be natural gas fired fully condensing, and fire tube design. Power burner shall have full modulation (the minimum firing rate shall not exceed 112,000 BTU/HR input. Boilers that have an input greater than 112,000 BTU/Hr at minimum fire will not be considered) and discharge into a positive pressure vent. Boiler efficiency shall increase with decreasing load (output), while maintaining setpoint. Boiler shall be factory-fabricated, factory-assembled and factory-tested, fire-tube condensing boiler with heat exchanger sealed pressure-tight, built on a steel base, including insulated jacket, flue-gas vent, combustion-air intake connections, water supply, return and condensate drain connections, and controls.

        - Heat Exchanger: The heat exchanger shall be constructed of 439 stainless steel fire tubes and tubesheets, with a one-pass combustion gas flow design. The fire tubes shall be a flatten 0.976” x 0.256” Channel, with no less than 0.0394” wall thickness. The upper and lower 439 stainless steel tube sheet shall be no less than 0.0984” thick. The pressure vessel/heat exchanger shall be welded construction. The heat exchanger shall be ASME stamped for a working pressure not less than 30 psig. Access to the tubesheets and heat exchanger shall be available by burner and exhaust manifold removal. Minimum access opening shall be no less than 4-inch diameter.

        - Pressure Vessel: The pressure vessel shall have a maximum water volume of 7 gallons. The boiler water pressure drop shall not exceed 3.0 psig at 38 gpm. The boiler water connections shall be 1 ½ -inch male NPT threaded connection. The pressure vessel shall be constructed of 439 stainless steel, with a .0984-inch (2.5MM) thick wall. Inspection openings in the pressure vessel shall be in accordance with ASME Section IV pressure vessel code. The boiler shall be designed so that the thermal efficiency increases as the boiler firing rate decreases.

        - Modulating Gas Venturi, Burner, and Pre-Mix Blower, The boiler burner shall be capable of a 3.6-to-1 turndown ratio of the firing rate without loss of combustion efficiency or staging of gas valves. The burner shall produce less than 12 ppm of NOx corrected to 3% excess oxygen. The unit shall be certified by the South Coast Air Quality Management District (SCAQMD) as compliant with Rule 1146.2 for boilers and water heaters less than or equal to 2 MBTUs, and the Texas Commission on Environmental Quality (TCEQ) as being compliant with Section 117.465 for boilers and water heaters less than or equal to 2 MBTUs. The burner shall be metal-fiber mesh covering a stainless steel body with spark ignition and flame rectification. All burner material exposed to the combustion zone shall be of stainless steel construction. There shall be no moving parts within the burner itself. A variable speed pre-mix blower and gas venturi shall meter the air and fuel input. The pre-mix blower shall be used to ensure the optimum mixing of air and fuel before the burner.

        - Minimum IBR boiler efficiency shall be 95.1%

        - The exhaust manifold shall be constructed of corrosion resistant 316 stainless steel with a four-inch diameter flue connection. The exhaust manifold shall have a collecting reservoir and a gravity drain for the elimination of condensation.

        - Blower. The boiler shall include a variable-speed, DC centrifugal fan to operate during the burner firing sequence and pre-purge the combustion chamber.

          - Motors: Blower motors shall comply with requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

- Motor Sizes: Minimum size as indicated. If not indicated, large enough so driven load will not require a motor to operate in the service factor range above 1.0.

        - Ignition: Ignition shall be via spark ignition with 100 percent main-valve shutoff and electronic flame supervision.

      - CONTROLS

        - Refer to Division 23, Section “Instrumentation and Control of HVAC.”

        - The boiler control system shall be a TriMax Control Panel.

        - The combustion safeguard/flame monitoring system shall use spark ignition and a rectification-type flame sensor.

        - The control panel hardware shall support remote communications via MODBUS.

        - The controls shall annunciate boiler and sensor status and include extensive self-diagnostic capabilities that incorporate a minimum of eight separate status messages and 18 separate fault messages that can be sent to a building automation system

        - TriMax Controller shall have a built-in sequencing function and be capable of controlling up to 6 units.  The controller shall have the ability to vary the firing rate and energy input of each individual boiler throughout its full modulating range to maximize the condensing capability and thermal efficiency output of the entire heating plant.  The ACS shall control the boiler outlet header temperature within +6ºF.  The controller shall be a PID type controller and uses Ramp Up/Ramp Down control algorithm for accurate temperature control with excellent variable load response.  The TriMax controller shall provide contact closure for auxiliary equipment such as system pumps and combustion air inlet dampers based upon outdoor air temperature.

        - Boiler Control Modes

          - Internal Set Point: Boiler shall include integral factory wired operating controls to control all operation and energy input of the boiler. Control of discharge water temperature shall be set through an internal set point with an adjustment of 60ºF to 194ºF.  The controller shall have the ability to vary boiler input throughout its full range to maximize the condensing capability of the boiler and without header temperature swings. The boiler will operate to maintain a constant header temperature outlet to +6ºF.

- Maximum efficiency shall be achieved at minimum firing input. Controls shall be fully field adjustable from 60ºF to 194ºF in operation. Main Header outlet temperature shall not be more than +6ºF from set point at any point of operation. The boiler shall have LCD display for monitoring of all sensors.

          - Outdoor Reset: Boiler shall include integral factory wired operating controls to control all operation and energy input of the boiler plant. The controller shall have the ability to vary boiler input throughout its full range to maximize the condensing capability of the boiler and without header temperature swings. The boiler will operate to vary header temperature set point on an inverse ratio in response to outdoor temperature to control discharge temperature +6ºF.

          - 0VDC to 10VDC BMS Control: A Boiler Management System (BMS) shall send a 0VDC to 10 VDC signal to control all operation and energy input of the boiler. The boiler will operate to vary firing rate linearly as an externally applied 0VDC to 10VDC mA signal is supplied to the Controller.

        - The Boiler Control System shall have a Boost Feature that if the call for heat is not satisfied in an adjustable time setting the set point will be raised by 18 ºF for each time period that the call for heat is not satisfied until the maximum boiler operating set point is reached.

        - The boiler control system shall incorporate the following additional features for enhanced external system interface:

          - Domestic Water Priority Feature

          - Domestic Water Pump Control

          - Primary Pump Control

            - Continuous operation

            - Activation when there is a call for heat

          - Inlet temperature sensor

          - Optional External limits - auto reset

          - Optional External Limits – manual reset

          - Fault relay for remote fault alarm

      - ELECTRICAL POWER

        - Controllers, Electrical Devices and Wiring: Electrical devices and connections are specified in Division 26 sections.

        - Single-Point Field Power Connection: Factory-installed and factory-wired switches, motor controllers, transformers and other electrical devices shall provide a single-point field power connection to the boiler.

        - Electrical Characteristics:

          - Voltage: 	120 V

          - Phase: 	Single

          - Frequency: 	60 Hz

          - 15 Amp Service

      - VENTING

        - The exhaust vent shale be PVC, CPVC, PPs Polypropylene or UL-listed vents of Al 29-4C stainless steel must be used with boilers.

        - The minimum exhaust vent duct size for each boiler is four-inch diameter.

        - Combustion-Air Intake: Boilers shall be capable of drawing combustion air from the outdoors via a metal or PVC duct connected between the boiler and the outdoors.

        - The minimum sealed combustion air duct size for each boiler is four-inch diameter.

        - Follow guidelines specified in manufacturer’s venting guide.

      - SOURCE QUALITY CONTROL

        - Burner and Hydrostatic Test: Factory adjust burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen emissions and carbon monoxide in flue gas, and to achieve combustion efficiency. Perform hydrostatic testing.

        - Test and inspect factory-assembled boilers, before shipping, according to ASME Boiler and Pressure Vessel Code.

          - If boilers are not factory assembled and fire-tested, the local vendor is responsible for all field assembly and testing.

        - Allow Owner access to source quality-control testing of boilers. Notify Architect fourteen days in advance of testing.

- EXECUTION

      - EXAMINATION

        - Examine piping and electrical connections to verify actual locations, sizes and other conditions affecting boiler performance, maintenance and operations.

          - Final boiler locations indicated on Drawings are approximate. Determine exact locations before roughing-in for piping and electrical connections.

        - Examine mechanical spaces for suitable conditions where boilers will be installed.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - BOILER INSTALLATION

        - Install boilers level on concrete bases. (If the floor mount kit is supplied) Concrete base is specified in Division 23 Section "Common Work Results for HVAC," and concrete materials and installation requirements are specified in Division 03.

        - Install gas-fired boilers according to NFPA 54.

        - Assemble and install boiler trim.

        - Install electrical devices furnished with boiler but not specified to be factory mounted.

        - Install control wiring to field-mounted electrical devices.

      - CONNECTIONS

        - Piping installation requirements are specified in other Division 23 sections. Drawings indicate general arrangement of piping, fittings and specialties.

        - Install piping adjacent to boiler to permit service and maintenance.

        - Install piping from equipment drain connection to nearest floor drain. Piping shall be at least full size of connection. Provide an isolation valve if required.

        - Connect gas piping to boiler gas-train inlet with unions. Piping shall be at least full size of gas train connection. Provide a reducer if required.

        - Connect hot-water piping to supply and return boiler tappings with shutoff valve and union or flange at each connection.

        - Install piping from safety relief valves to nearest floor drain.

        - Boiler Venting

          - Install flue venting kit and combustion-air intake.

          - Connect venting full size to boiler connections. [Comply with requirements in Division 23 Section "Breechings, Chimneys and Stacks."]

        - Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

        - Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

      - FIELD QUALITY CONTROL

        - Perform tests and inspections and prepare test reports.

          - Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies and equipment installations, including connections, and to assist in testing.

        - Tests and Inspections

          - Installation and Startup Test: Perform installation and startup checks according to manufacturer's written instructions.

          - Leak Test: Perform hydrostatic test. Repair leaks and retest until no leaks exist.

          - Operational Test: Start units to confirm proper motor rotation and unit operation. Adjust air-fuel ratio and combustion.

          - Controls and Safeties: Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

- a.	Check and adjust initial operating set points and high- and low-limit safety set points of fuel supply, water level and water temperature.

- b.	Set field-adjustable switches and circuit-breaker trip ranges as indicated.

        - Remove and replace malfunctioning units and retest as specified above.

        - Occupancy Adjustments: When requested within 2 months of date of Substantial Completion, provide on-site assistance adjusting system to suit actual occupied conditions. Provide up to two visits to Project during other than normal occupancy hours for this purpose.

END OF SECTION 235216